| Automatic Temperature Controller SU-105 User Manual |
| --- |
| Model | Temperature range | Output |
| SU-105 IP | IC | (-50.0℃~150℃) | Main/Aux(DC12V) Main/Aux(Relay) |
| ※ Thank you for purchasing a SamWon ENG CO.,LTD product. This manual contains the information on how to use the product. Keep it in a safe place and refer to it whenever necessary. |

| Display Unit | Displays a current temperature or user-set temperature |
| --- | --- |
| Main/Aux Output | Indicates the main or auxiliary output is ON or OFF |
| Set key Up key Down key |  | Setting button Increment button Decrement button |

▶Power controller for heaters and coolers

Hysteresis 0.0~9.9 degree C., 0~240 second delay timer, Normal/Reverse selection.

▶Contains a digital timer to control defrosting. Range: 1~999 minute.

▶User configuration control

˚You can specify a valid temperature range that a user is allowed to use.

˚You can prevent a user from changing the setting of hysteresis, delay time,

and normal/reverse.

▶Turn on the power and wait until the current

temperature appears on the display.

▶Press set key once and notice

the display unit blinks.

▶Use Up or Dn key to change the setting.

If you hold down a key for longer than

4 seconds, the number will increase or

decrease rapidly.

Note: The selectable range might be

limited by User configuration control.

▶Store the setting in memory by pressing

set key for longer than 5 seconds.

▶The unit show the current temperature

and start working.

▶The main output uses terminal 7 ~ 9.

Note: For information on Auxiliary

output (Alarm/Timer), refer to Section

13. How to set Alarm Output.

① How to connect sensors

▶When connecting sensors, use the

following figure. If you connect the

lines incorrectly or a different type

of sensors, the display unit will

show ‘Err’.

② Sensor line extension

▶A Pt100 sensor line can be extended

up to 100 M.

▶An IC/Humidity sensor line can be

extended up to 500 M.

▶You MUST use a shielded line to prevent

the noise when extending a line.

③ Sensor input correction (when current temperature is incorrect)

▶Press set key for longer than 5 seconds, when the display unit shows a current

temperature

▶Release the key when you see diF. Select rSt by pressing set key.

▶Select a correction temperature using Up or Dn key.

▶Store the setting in memory by pressing the set key for longer than 5 seconds.

For example,

| Current temperature |  | rSt corrected temperature |  | Displayed current temperature |
| --- | --- | --- | --- | --- |
| 20.0 ℃ | + + | -5.0 ℃ | = = | 15.0 ℃ |
| 20.0 ℃ |  | 10.0 ℃ |  | 30.0 ℃ |

| Voltage | AC220V (50/60Hz) ±10% (AC110V,option) |
| --- | --- |
| Power | 5VA or less |
| Input Sensor | K(CA) with a load/line of 100Ω or less PT100Ω with a load/line of 5Ω or less |
| Accuracy | K(CA):display the value ±0.5% +1digit Pt100:display the value ±0.2% +1digit |
| Hysteresis | 0.1℃ ~ 9.9℃ |
| Control output | Relay Output:AC250V 5A Relay life time:300,000 or grater |
| Control operation | ON/OFF Control |
| Setting Methode | Digital Methode with Up or Down key |
| Etc. | Sensor input correction,Delay timer,Normal/Reverse selection,Defrosting Timer |
| Environment Temperature | 0℃ ~ 50℃ |
| Environment humidity | 85% RH or less |

▶To change hysteresis, press SET key for longer than 5 seconds. Release the key when

the display unit shows diF.

▶Set the configuration as following using Up and Dn keys.

| User setting |  | Item | Setting | Description |
| --- | --- | --- | --- | --- |
|  |  | diF | 0.1~9.9 | Prevent relay vibration from hysteresis |

▶Store the setting in memory by pressing the SET key for longer than 5 seconds.

▶Description of ON/OFF control based-on hysteresys value

| User setting |  | Item | Setting | Description |
| --- | --- | --- | --- | --- |
|  |  | tyP | C | Controls the cooler (Reverse output) |
|  |  |  | H | Controls the heater (Normal output) |

① Cooler On/Off control

▶When the current temperature becomes higher than a configured temperature, the main

output relay turns on.

▶You can use a delay timer to protect a compressor.

② Heater On/Off control

▶When the current temperature becomes lower than a configured temperature, the main

output relay turns on.

Note: In general, the B contact of a relay is used for reverse output. In this case, be

cautious since the contact B is ON even though the power to the unit is turned off.

For example)

Heater control                        Cooler control

|  | OFF |  | OFF |  |  | OFF |  | OFF |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ON |  | ON |  |  | ON |  | ON |  |

SV=50.0,diF=5.0,dLt=0,tyP=H   SV=-25.0,diF=5.0,dLt=0,tyP=C

▶In order to change the delay timer setting, press SET key for longer than 5 seconds

while the display unit shows the current temperature. Release the key when the display

unit shows diF. Press SET key several times to select dLt.

▶After selecting a value using Up or Dn key, press SET key to store the setting in the

memory.

Description: When the delay time expires, the output turns on.

| User setting |  | Item | Setting | Description |
| --- | --- | --- | --- | --- |
|  |  | dLt | 0~240sec | Output become on after specified time |

▶How the delay timer works

Case: the delay time is 0 second => the relay turns on as soon as output signal arrives.

Case: the delay time is 5 seconds => the relay turns on after 5 seconds upon the arrival o output signal.

▶The following diagram shows configurable items. Select an item by

pressing set key.

▶Make a note of the factory default settings before changing any one of them. Before

making any change, understand and verify the validity of your setting(s).

▶Invalid factory settings may require service from the manufacturer.

① You can prevent a user from changing a pre-set configuration.

▶Turn off the power. Turn on the power while pressing set key. Keep pressing set key

until you see StH on the display unit. Release the key when the display unit shows StH.

▶Press set key several times to select Loc. Set the configuration as following using Up

and Dn keys

| Factory Setting |  | Item | Setting | Description |
| --- | --- | --- | --- | --- |
|  |  | Loc | 0 | Unlocked – a user can change settings |
|  |  |  | 1 | Locked – a user can’t change a pre-set configuration |

▶Press set key for longer than 5 seconds to save the configuration.

Note: Once locked, a user can’t change a pre-set configuration by pressing set key for

longer than 5 seconds. The unit must be unlocked before a user can change the pre-set

configuration.

② You can specify the range of temperature that a user can set.

▶Turn off the power. Turn on the power while pressing set key. Keep pressing set key

until you see StH on the display unit.

▶Press set key several times to select StL. Set the configuration as following using Up

and Dn keys.

| Factory Setting |  | Item | Setting | Description |
| --- | --- | --- | --- | --- |
|  |  | StH | 50.0 | The highest value for high temperature is 50 degree. |
|  |  | StL | 40.0 | The lowest value for low temperature is 40 degree. |

▶Press set key for longer than 5 seconds to save the configuration.

Note: After this configuration, the main temperature can be set only within the range of 40

to 50 degree.

① Set the auxiliary relay output to Alarm Output

▶The auxiliary relay selects either Alarm Output or Timer Output. Set the relay to Alarm

Output. (Alarm Output is factory default setting)

▶You MUST turn off the power to change the factory settings.

▶Turn on the power while pressing set key. And keep pressing the set key.

▶Release the set key when the display shows StH.

▶Press set key several times until you see tyP.

▶Set the configuration as following using Up and Dn keys

| Factory Setting |  | Item | Setting | Description |
| --- | --- | --- | --- | --- |
|  |  | tyP | H or C | Use Auxiliary output as Alarm output (C = Alarm High, H = Alarm Low) |

▶Store the setting in memory by pressing the set key for longer than 5 seconds.

②How to set Alarm Output Temperature

▶When the display shows current temperature, press set key for longer than 5 seconds.

Release the set key when the display shows diF.

▶If Pro is not displayed, you have to the auxiliary output to Alarm Output. Refer to the

item 1) above.

▶Select Pro by pressing set key several times.

▶Set the configuration as following using Up and Dn keys

| User Setting |  | Item | Setting | Description |
| --- | --- | --- | --- | --- |
|  |  | Pro | 100.0 | Alarm Output Temperature is set to 100 degree C. |

▶Store the setting in memory by pressing the set key for longer than 5 seconds.

③ How to set Alarm High or Low

▶To change the factory setting, you MUST turn off the power.

▶Turn the power on while pressing set key. And keep pressing the set key.

▶Release the key when the you see StH in the display unit.

▶Select tyP by pressing set key several times.

▶Set the configuration as following using Up and Dn keys

than the alarm temperature

▶Press set key for longer than 5 seconds to save the configuration.

| Factory Setting |  | Item | Setting | Description |
| --- | --- | --- | --- | --- |
|  |  | tyP | H | The output is turn on when the current temperature becomes lower |
|  |  |  | C | The output is turn off when the current temperature becomes higher than the alarm temperature |

④ How to disable the alarm output

▶When you want to turn off alarm relay output, follow the procedure described below.

▶Press set key for longer than 5 seconds when the display shows a current temperature.

Release the key when you see diF.

▶Press set key several times to select Pro.

▶Select either the highest value or lowest value using Up or Dn key.

| User setting |  | Item | Setting | Description |
| --- | --- | --- | --- | --- |
|  |  | Pro | oFF | This configuration disables the alarm output. |

▶Press SET key for longer than 5 seconds to save the configuration.

① How to set the auxiliary relay to the timer output

▶The auxiliary relay selects either the alarm output or timer output. As a factory

setting, the relay is set to the alarm output.

▶To change the factory setting, you MUST turn off the power.

▶Turn the power on while pressing set key. And keep pressing the set key.

▶Release the key when the you see StH in the display unit.

▶Select tyP by pressing set key several times.

▶Set the configuration as following using Up and Dn keys

| Factory setting |  | Item | Setting | Description |
| --- | --- | --- | --- | --- |
|  |  | tyP | t | Use the auxiliary relay as the timer output |

▶Press set key for longer than 5 seconds to save the configuration.

② How to set timer

▶Press set key for longer than 5 seconds when the display shows a current

temperature. Release the key when you see diF.

▶Press set key several times to select On. If ON does not appear, the auxiliary output is

not selected as the timer output. See 1) How to set the auxiliary relay to the timer output

▶Set the configuration as following using Up and Dn keys

| User setting |  | Item | Setting | Description |
| --- | --- | --- | --- | --- |
|  |  | on | 5 | The output will be ON for 5 minutes after a OFF period of 15 minutes |
|  |  | oFF | 15 | The output will be OFF for 15 minutes after a ON period of 5 minutes. |

▶Press set key for longer than 5 seconds to save the configuration.

③Description of the pulse cycle

Note: Periodic timer is operated separatory operated from temperature controller

▶Install the unit in an environment where

- the temperature is relatively constant,

- there is no corrosive gas,

- the humidity is normal, and

- there is no excessive dust and electric noise.

▶Wire (or line) connections

Sensor line is sensitive to noise from high-voltage power line. Use a separate pipe.

▶For applications where bodily injury or property damage can occur, you  connect

the product using a double safety device.

# Text boxes

1. Description of display

set

up

dn

2.Capability and applications of the product

3.How to set main output

<Main Output Terminal>

Coil

Magnet

메인

전원

작동

기계

AC

220V

Pow

er

Mac

hine

<Display Current>

①Red/White ②Shield/Black

4. How to connect sensors

①White②Black③Black

5.External dimension

50

45

-20

-25

9.Delay timer setting

10.User configurable settings

Aux output setting

diF

dLt

tyP

Normal/Reverse Control

Hysteresis

0.1℃~ 9.9℃

Delay time

0~240sec

Normal/Reverse selection

C:Coller,H:Heater

rSt

Sensor input correction

-50.0~+50.0

Press set key when the display unit shows a current temperature

Press set key for longer than 5 seconds to save the configuration.

StH

StL

Upper limit temperature

Temperature Range for each sensor

Keep pressing set key until you

see StH on the display unit.

Release the key when the

display unit shows StH.

※ diF가 나타나면 다시 하세요

Loc

Lower limit temperature

Temperature Range for each sensor

Locking Function for user

0:Release, 1:Locking

70

34

76

28

PANEL CUT OUT

70

(unit: mm)

6.Product specification

SV

OFF

ON

15

10

SV

OFF

ON

15

10

SV

ON

OFF

15

10

SV

ON

OFF

15

10

tyP=H

Heater(Normal)

tyP=C

Cooler(Reverse)

hysteresis diF=1.0

hysteresis diF=2.0

8. Normal/Reverse output

delay time when dLt=0

delay time when dLt=5

0sec

5sec

10sec

Relay Off                  Relay On

Relay Off             Relay On

<Rear panel terminal>

| Sensor | Aux output |  | Main output | Power |
| --- | --- | --- | --- | --- |
| B | W | sh | RELAY 3A |  | RELAY 3A | AC 220V |
| R/W | B |  |  |  |  |  |
| ① | ② | ③ | ④ | ⑤ | ⑥ |  | ⑦ | ⑧ | ⑨ | ⑩ | ⑪ |

###### A                B      B’

RTD

+     -

###### TC

| Sensor | Aux output |  | Main output | Power |
| --- | --- | --- | --- | --- |
| B | W | sh | RELAY 3A |  | RELAY 3A | AC 220V |
| R,W | B |  |  |  |  |  |
| ① | ② | ③ | ④ | ⑤ | ⑥ |  | ⑦ | ⑧ | ⑨ | ⑩ | ⑪ |

13.How to set Alarm Output (Auxiliary output)

Aux Output(Alarm)

Aux Output(Timer)

Pro

on

Timer on setting

0~999Min

oFF

Timer off setting

0~999Min

Alarm Setting Temp.

Temperature Range

for each sensor

Factory Setting Items

11.Factory default settings

diF

dLt

tyP

Alarm hysteresis

0.1℃~ 9.9℃

Alarm delay timer

0~240sec

Aux output:Timer/Normal/Reverse Selection

C:Cooler,H:Heater(C:Upper Alarm,H:Lower Alarm),t:Timer

14.Timer setting

15min. Off      5min. On      15min. Off      5min. On

Pulse cycle

output while

on=5min,

oFF=15min

up

dn

set

on

℃

Up key

Set key

Display Unit

Down Key

Main Output

            - IC/HUM

            - Ca-K

7.Hysteresis setting

Turn off the power. Turn on the

power while pressing set key.

To go back to the top, press set key

Press set key for longer than 5 seconds to save the configuration.

12.Prevention of re-configuration and configuration lock

15. Installation

To go back to the top, press set key

Main output setting

Head Office and Factory : #703-4 Hwamokdong Gimhae Gyoungnam, South Korea

Phone : 82-055-321-3030/1   Fax : 321-3060

Homepage : http://31eng.co.kr/   E-mail : 31eng@paran.com

In Pursuit of Perfect Production for Customer Service Excellence.